## January 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-01-01
Inspection Date: |  |  | 2020-01-17 | 2020-01-24 | 2020-01-31 |  |  | Form Prepared by: ERM NC, Inc.
Inspector: (name) |  |  | Eric Slater | Eric Slater | Eric Slater |  | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes |  |  | y | y | N | Rill formation identified from ~10Jan20 rain event; mostly present at northwest portion of berm exterior on west/river side where slope appears to have bottom ash; max. ~3-inch deep | -prior to corrective action, monitor rill dimensions -use excavator to smooth outer side of berm | Thur., Jan 30th, 2020 | EJS
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes |  |  | N | N | N
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth. |  |  | N | N | N
Inspect for visual indications of animal burrowing activities along interior and exterior slopes. |  |  | N | N | N
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column. |  |  | N | N | N
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments. |  |  | N | N | N
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues. |  |  | N | N | N
ADDITIONAL NOTES: ERM/NS pumping water intermittently from basin over the top to a filter bag and not necessarily at the time/date of the inspection. Discharged water is sampled in accordance with the associated discharge permit.

## February 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-02-01
Inspection Date: | 2020-02-06 | 2020-02-13 | 2020-02-20 | 2020-02-27 |  |  |  | Form Prepared by: ERM NC, Inc.
Inspector: (name) | Eric Slater | Eric Slater | Eric Slater | Eric Slater |  |  | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes | N | N | N | N
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes | N | N | N | N
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth. | N | N | N | N
Inspect for visual indications of animal burrowing activities along interior and exterior slopes. | N | N | N | N
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column. | N | N | N | N
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments. | N | N | N | N
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues. | N | N | N | N
ADDITIONAL NOTES ERM/NS pumping water intermittently from basin over the top to a filter bag and not necessarily at the time/date of the inspection. Discharged water is sampled in accordance with the associated discharge permit.

## March 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-03-01
Inspection Date: | 2020-03-06 | 2020-03-13 | 2020-03-20 | 2020-03-27 |  |  |  | Form Prepared by: ERM NC, Inc.
Inspector: (name) | Chris Mettler | Eric Slater | Eric Slater | Eric Slater |  |  | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes | N | N | Y | Y |  | Up to ~4-inch deep rills in NW on outer berm wall from 1.6-inch rain on 19Mar20 (should smooth over) | Rills will be smoothed over as soon as logistically possible (It is desired to use heavy equipment.)
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes | N | N | N | N
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth. | N | N | N | N
Inspect for visual indications of animal burrowing activities along interior and exterior slopes. | N | N | N | N
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column. | N | N | N | N
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments. | N | N | N | N
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues. | N | N | N | N
ADDITIONAL NOTES

## April 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-04-01
Inspection Date: | 2020-04-03 | 2020-04-07 | 2020-04-16 | 2020-04-23 | 2020-04-30 |  |  | Form Prepared by: ERM NC, Inc.
Inspector: (name) | Eric Slater | Eric Slater | Eric Slater | Eric Slater | Eric Slater |  | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes | Y | Y | N | N | N | Up to ~4-inch deep rills in NW, SW on outer berm wall from 1.6-inch rain on 19Mar20 (should smooth over) | Rills were smoothed manually in the NW and the SW spot was reinforced with clay using an excavator on 15Apr20
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes | N | N | N | N | N
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth. | N | N | N | N | N
Inspect for visual indications of animal burrowing activities along interior and exterior slopes. | N | N | N | N | N
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column. | N | N | N | N | N
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments. | N | N | N | N | N
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues. | N | N | N | N | N
ADDITIONAL NOTES

## May 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-05-01
Inspection Date: | 2020-05-07 | 2020-05-14 | 2020-05-20 | 2020-05-29 |  |  |  | Form Prepared by: ERM NC, Inc.
Inspector: (name) | Eric Slater | Eric Slater | Eric Slater | Eric Slater |  |  | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes | N | N | N | N
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes | N | N | N | N
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth. | N | N | N | N
Inspect for visual indications of animal burrowing activities along interior and exterior slopes. | N | N | N | N
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column. | N | N | N | N
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments. | N | N | N | N
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues. | N | N | N | N
ADDITIONAL NOTES

## June 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-06-01
Inspection Date: | 2020-06-05 | 2020-06-12 | 2020-06-19 | 2020-06-23 | 2020-06-29 |  |  | Form Prepared by: ERM NC, Inc.
Inspector: (name) | Eric Slater | Eric Slater | Eric Slater | Eric Slater | Eric Slater |  | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes | N | N | N | N | N
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes | N | N | N | N | N
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth. | N | N | N | N | N
Inspect for visual indications of animal burrowing activities along interior and exterior slopes. | N | N | N | N | N
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column. | N | N | N | N | N
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments. | N | N | N | N | N
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues. | N | N | N | N | N
ADDITIONAL NOTES ERM/NS pumping water intermittently from basin over the top through a filter skid and not necessarily at the time/date of the inspection. Discharged water is sampled in accordance with the associated discharge permit. Ash basin undergoing closure activities.

## July 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-07-01
Inspection Date: | 2020-07-07 | 2020-07-14 | 2020-07-21 | 2020-07-28 |  |  |  | Form Prepared by: ERM NC, Inc.
Inspector: (name) | Eric Slater | Eric Slater | Eric Slater | Eric Slater |  |  | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes | N | N | N | N
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes | N | N | N | N
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth. | N | N | N | N
Inspect for visual indications of animal burrowing activities along interior and exterior slopes. | N | N | N | N
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column. | N | N | N | N
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments. | N | N | N | N
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues. | N | N | N | N
ADDITIONAL NOTES ERM/NS pumping water intermittently from basin over the top through a filter skid and not necessarily at the time/date of the inspection. Discharged water is sampled in accordance with the associated discharge permit. Ash basin undergoing closure activities, which includes excavation and consolidation of ash basin materials.

## August 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-08-01
Inspection Date: | 2020-08-07 | 2020-08-14 | 2020-08-21 | 2020-08-28 |  |  |  | Form Prepared by: ERM NC, Inc.
Inspector: (name) | Eric Slater | Eric Slater | Eric Slater | Eric Slater |  |  | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes | N | N | N | N
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes | N | N | N | N
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth. | N | Y | Y | N |  | vegetation > 6-inches in places | cut vegetation | 2020-08-24 | ES
Inspect for visual indications of animal burrowing activities along interior and exterior slopes. | N | N | N | N
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column. | N | N | N | N
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments. | N | N | N | N
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues. | N | N | N | N
ADDITIONAL NOTES ERM/NS pumping water intermittently from basin over the top through a filter skid and not necessarily at the time/date of the inspection. Discharged water is sampled in accordance with the associated discharge permit. Ash basin undergoing closure activities, which includes excavation and consolidation of ash basin materials. Interior of perimeter berm cleaned of residual ash materials on south and west sides. Outfall 002 structure area also removed of residual ash to the extent practical while staying in place. Probable last full month of inspections, as proposed future work includes berm and outfall removal.

## September 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-09-01
Inspection Date: | [7 empty] | Form Prepared by: ERM NC, Inc.
Inspector: (name) | [6 empty] | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth.
Inspect for visual indications of animal burrowing activities along interior and exterior slopes.
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column.
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments.
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues.
ADDITIONAL NOTES

## October 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-10-01
Inspection Date: | [7 empty] | Form Prepared by: ERM NC, Inc.
Inspector: (name) | [6 empty] | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth.
Inspect for visual indications of animal burrowing activities along interior and exterior slopes.
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column.
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments.
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues.
ADDITIONAL NOTES

## November 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-11-01
Inspection Date: | [7 empty] | Form Prepared by: ERM NC, Inc.
Inspector: (name) | [6 empty] | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth.
Inspect for visual indications of animal burrowing activities along interior and exterior slopes.
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column.
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments.
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues.
ADDITIONAL NOTES

## December 2020
GTEC Inactive Ash Basin - Weekly Inspection Form
MONTH: | 2020-12-01
Inspection Date: | [7 empty] | Form Prepared by: ERM NC, Inc.
Inspector: (name) | [6 empty] | For Use by: Grand Tower Energy Center, LLC File 230.0319
| PROBLEM | PROBLEM | PROBLEM | PROBLEM | PROBLEM | COMPLETE ONLY IF PROBLEM FOUND
INSPECTION | FOUND | FOUND | FOUND | FOUND | FOUND | DESCRIBE | DESCRIBE | DATE OF | INSPECTOR
ITEM | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | (Y OR N) | PROBLEM | CORRECTIVE | CORRECTIVE | INITIALS
[7 empty] | ACTION TAKEN | ACTION
Inspect for any appearances of actual or potential structural weakness
Inspect for visual indications of erosion; formation of rills or gullies; along interior and exterior slopes
Inspect for visual indications of surface soil "sluffing" or sliding along interior and exterior slopes
Inspect vegetation height; should be maintained less than 6-inches and no woody vegetation (tree) growth.
Inspect for visual indications of animal burrowing activities along interior and exterior slopes.
Inspect the discharge of all outlets of hydraulic structures which pass through the basin dike for abnormal discoloration, flow or discharge of debris or sediment.
Outfall at south end of basin; inspect for visual signs of discoloration of discharge water. If no discharge is observed, place "N/A" in Problem Found Column.
Outfall at south end of basin; inspect for visual signs of sedimentation from discharge. If sediment is observed, describe color and texture of sediments.
Visually inspect the outfall structure at the south end of the basin for structural distress or related operational issues.
ADDITIONAL NOTES