| Illinois Environmental Protection Agency BOW-Permits #15-CCR Coordinator 2520 W Iles Avenue P.O. Box 19276 Springfield, IL 62794-9276 | Date 23 January 2026 |
| --- | --- |
|  | Subject Fifteenth Post-Closure Groundwater Monitoring Report Fourth Quarter 2025 Grand Tower Energy Center Closed Coal Combustion Residuals Impoundment 1820 Power Plant Road Grand Tower, IL 62942 BOW ID No. W0770400003 |
|  | reference ERM Project No. 0761817 |

To Whom it May Concern:

Environmental Resources Management Inc. (ERM) is submitting this report which provides the results and findings of the Grand Tower Energy Center (GTEC) quarterly post-closure groundwater sampling and closed coal combustion residuals (CCR) impoundment inspection event conducted during the fourth quarter 2025 at the GTEC facility located at 1820 Power Plant Road, Grand Tower, IL (the “Site”). The fourth quarter groundwater sampling event took place between 19 November and 20 November 2025, and the closed impoundment inspection event was conducted on 20 November 2025. A Site location map is provided in Figure 1.

The fourth quarter 2025 groundwater sampling event was performed in accordance with the post-closure groundwater monitoring program presented within the Grand Tower Operating Permit Application (OPA) submitted to the Illinois Environmental Protection Administration (IEPA) on 28 October 2021, as modified in accordance with the Consolidated IEPA Comments dated 17 March 2022 and included in the updated Closure/Post-Closure Plan submitted to the IEPA with the 27 February 2024 response to the 23 January 2023 OPA comment letter from the IEPA. The purpose of the sampling event was to continue the initial five-year period of quarterly groundwater monitoring for the evaluation of the concentration and areal distribution of impacts related to the closed CCR impoundment in Site groundwater. The parameters detected in the groundwater are associated with the historical CCR impoundment, which was capped and closed in 2020. The quarterly results include a summary of field activities,

laboratory analytical, and documentation of other associated Site activity, as necessary.

Fourth quarter 2025 site activities, performed in accordance with the proposed post-closure groundwater monitoring program, the results of which are summarized below, included:

- Inspection of the final cover system of the closed CCR impoundment;

- Inspection of the groundwater monitoring well array; and

- Groundwater monitoring activities.

## Quarterly Closed CCR Impoundment Inspection

During the fourth quarter of 2025, an inspection of the closed CCR impoundment cover system and associated features was completed, and the full quarterly inspection report can be found in Appendix A. Woody vegetation (up to 1” diameter) was noted within the riprap around the toe of the side slope of the CCR impoundment cap faces. Additionally, woody vegetation was noted in the outfall channel, which allows discharge of water within the basin at the foot of the closed CCR side slope to the Mississippi River via an unnamed drainage ditch. Erosional channels on the west, south, and east faces were noted as less than 6” deep in the deepest locations and will be monitored during subsequent inspection events and recommendations made to repair these features, if necessary. No significant degradation or issues were noted associated with the overall closed CCR impoundment cover system.

## Quarterly Monitoring Well Inpsection and Gauging

During the fourth quarter of 2025, monitoring well inspections were conducted. The monitoring well protectors and casings were inspected for damage and/or signs of settling that might impact the integrity of the surface seals and/or the well casings. All monitoring wells were observed to be intact during the quarterly monitoring well inspections. The inspection tasks also included gauging total depths as well as static groundwater elevations in all site wells. Both measurements were referenced from the top of casing (TOC) at each of the Site monitoring wells. Total depth and groundwater level measurements were obtained from the monitoring wells using a water level meter with an accuracy of 0.01 foot. The quarterly monitoring well inspection forms can be found in Appendix B. Based upon these measurements, a shallow groundwater contour map for the Site was developed for the fourth quarter of 2025. The groundwater gradient is primarily from east to west towards the Mississippi River except during times of flooding events that may cause a reverse flow from west to east for a short period of time (Natural Resource Technology, Phase 1 Hydrogeologic Assessment Report, March 2013). Figure 2 shows monitoring well locations with a groundwater contour and groundwater gradient direction arrow(s), groundwater elevations at each monitoring well, and the Mississippi River elevation at the time of groundwater level gauging.

## Quarterly Groundwater Monitoring

The Groundwater Protection Standards (GWPS) for the Site are those provided in 35 IAC §845.600(a). Assessment of corrective measures began on 16 June 2022 with the commencement of the initial post-closure groundwater sampling event. During the fourth quarter 2025 sampling event, 12 monitoring wells (APW-01R, APW-02, APW-03, APW-04, APW-05R, APW-06D, APW-06S, APW-07, APW-08, APW-09, APW-10D, and APW-10S) were sampled.

The monitoring wells were purged prior to sampling using a submersible pump according to United States Environmental Protection Administration (USEPA) low flow purging and sampling procedures (“Low Stress Purging and Sampling Procedure for the Collection of Groundwater Samples from Monitoring Wells” revised September 19, 2017). The pump intake was placed within the screened interval of each monitoring well sampled and stabilization measurements were collected using a calibrated YSI ProDSS meter during purging activities for the collection of pH, specific conductivity, temperature, dissolved oxygen, and oxidation reduction potential (ORP) readings. Turbidity readings were also collected from each monitoring well using a Hach 2100Q Turbidimeter. Well purging continued until stabilization of each field parameter was achieved according to USEPA guidelines for low-flow sampling. Once the field parameters stabilized, the YSI meter was disconnected, and groundwater samples were collected for analysis using the same dedicated polyethylene tubing that was used to purge the well. Field parameter measurements collected during this sampling event were recorded on field data forms. Copies of the field data forms are included in Appendix C.

The groundwater samples collected were placed in laboratory-provided sample containers for analysis by Pace Analytical located in Mt. Juliet, TN, which is an IEPA-approved laboratory. Samples were transported via FedEx under chain-of-custody procedures to the laboratory for analytical testing within laboratory provided coolers containing ice. The laboratory analytical reports for the fourth quarter 2025 sampling event are included in Appendices D & E.

In accordance with the 3 March 2022 draft comments received from the IEPA Groundwater Section associated with the post-closure groundwater monitoring program contained in the OPA submitted to the IEPA on 28 October 2021, the IEPA evaluates the efficacy of corrective actions for closed CCR impoundments through the comparison of the groundwater analytical results to the GWPS contained in 35 IAC §845.600. Under 35 IAC §845.600, the following groundwater parameters are to be monitored:

| - Antimony | - Chloride | - Mercury | - TDS |
| --- | --- | --- | --- |
| - Arsenic | - Chromium | - Molybdenum | - Radium 226/228 |
| - Barium | - Cobalt | - pH | - Calcium |
| - Beryllium | - Fluoride | - Selenium | - Turbidity |
| - Boron | - Lead | - Sulfate |  |
| - Cadmium | - Lithium | - Thallium |  |

## Groundwater Analytical Results

The analytical results for the post-closure groundwater sampling event conducted during the fourth quarter 2025 are presented in Table 1. During the fourth quarter 2025 sampling event, the following analytes and/or field parameters were detected in the listed wells above the GWPS:

- Arsenic: APW-10S

- Boron: APW-02, APW-03, APW-05R, APW-06D, APW-06S

- Calcium: APW-02, APW-03, APW-04, APW-05R, APW-06D, APW-06S, APW-07, APW-08, APW-10D, APW-10S

- Lithium: APW-02, APW-06S

- Molybdenum: APW-02, APW-05R, APW-06S

- Sulfate: APW-02

- Turbidity: APW-01R, APW-02, APW-04, APW-06S

APW-10S, located approximately one-half mile south of the closed CCR impoundment, continues to exhibit elevated arsenic concentrations. However, the occurrence of arsenic in this well is not considered to be related to the closed CCR impoundment due to its distance and location hydraulically side gradient in relation to the Site. Additionally, the monitoring wells located between the closed CCR impoundment (APW-03, APW-07, APW-08, APW-09, and APW-10D) and APW-10S do not exhibit arsenic concentrations above the GWPS.

The GTEC closed CCR impoundment is currently in Corrective Action Monitoring (CAM). As reported in the 2024 Annual Groundwater Monitoring Report - Grand Tower Energy Center submitted by ERM and dated January 2025, statistical analysis conducted on the data collected from the first eleven quarters of post-closure monitoring (2nd quarter 2022 through 4th quarter 2024) indicates that arsenic, boron, calcium, lithium, molybdenum, and sulfate exceed the calculated background concentrations and the IEPA GWPS established in 35 IAC Section 845.600 in monitoring wells at the Site. Statistical analysis of the groundwater sampling results will continue to be completed on an annual basis to evaluate if statistically significant increases or decreases have occurred after cap and closure occurred in 2020 in accordance with 35 IAC Section §845.640(f). In accordance with 35 IAC Section §845.550(a), an Annual Groundwater Monitoring and Corrective Action Report will be submitted for 2025 on or before 31 January 2026.

At the end of the current five-year monitoring and reporting post-closure time frame, a groundwater performance monitoring report will be submitted to IEPA to either demonstrate restoration of groundwater quality to Class I standards or present a continued groundwater monitoring plan for an additional five years. In addition, the results will be compared to the modeled concentrations to evaluate if a decreasing trend, as defined through modeling, is occurring at the predicted rate. Significant changes from the model results will lead to additional calibration and assessment of future expected rates of decrease for the constituents of concern (COCs).

Summary and Conclusions

Based upon the results of the fourth quarter 2025 groundwater sampling event, well inspection, and closed CCR impoundment inspection, the following observations and conclusions have been made:

- Similar to the groundwater sampling results obtained during the eight pre-closure sampling events in 2017 to 2018, and 14 post-closure groundwater sampling events, concentrations of COCs above the GWPS continue to be detected at well locations downgradient of the closed CCR impoundment.

- Boron has historically been the key indicator for corrective action and continued monitoring of groundwater at the Site. Incorporating data from the eight rounds of pre-closure groundwater sampling conducted during 2017 and 2018, as well as the 14 post groundwater monitoring events, boron concentrations have shown a decreasing trend in Site monitoring wells.

- During the Q4 2025 event, woody vegetation was observed in the riprap, less than 1” thick in diameter. Continued monitoring of woody growth, and treatment recommendation will take place during subsequent quarterly sampling events.

- If you have any questions, please contact me at (314) 733-4490.

Sincerely,

Jarred Schmidt 	     Wayne T. Sicora, P.E.

Principal Consultant	     Principal Engineer

Attachments

cc: Mr. Brandon Stempa, Perdomo Worldwide - Grand Tower Energy Center (electronic)

# FIGURES

- Tables

- Appendix A	Fourth Quarter 2025 CCR Impoundment Inspection Report

- Appendix B	Fourth Quarter 2025 Groundwater Monitoring Well Inspection Forms

- Appendix C	Fourth Quarter 2025 Field Data Forms

- Appendix D	Fourth Quarter 2025 Laboratory Analytical Report

# Appendix E 	Fourth Quarter 2025 Radiological Laboratory Analytical Report